## Coal details 660
| Name | [16 empty] | Instructions for filling the format
| Enter 1st day of reporting month ===> |  |  | 2025-02-01 |  | FAC-II |  | Year | 2024 |  | Days | 28 | [5 empty] | 1) Only red figures to be filled
2) Figures of CV in table A & B - CIMFR results. If not available, plant lab results
| Name of the TPS : Bhusawal Thermal Power Station |  | Stage IV | 660 MW | [5 empty] | Month | 2025-02-01 | [6 empty] | 3) Figures of coal details in table A & B should be as reported in FAC
[12 empty] | 45688 | 45716
A | Coal stock and receipt for station | [16 empty] | 4) Format is aimed at analysis of the gap between heat available for firing as per MERC
| S.N | Source | Opening coal stock |  |  |  |  | Receipt |  |  |  |  | Opening stock + Receipt |  |  |  |  | regulations and heat utilised for generation considering coal firing capacity and achievable heat rate
|  |  | Qty (MT) | Landed cost (Rs/MT) | As billed Eq CV (loading end) Kcal/kg | Eq CV (Unloading end) Kcal/kg | ARB CV (Kcal/kg) | Qty (MT) | Landed cost (Rs/MT) | As billed Eq CV (loading end) Kcal/kg | Eq CV (Unloading end) Kcal/kg | ARB CV (Kcal/kg) | Qty (MT) | Landed cost (Rs/MT) | As billed Eq CV (loading end) Kcal/kg | Eq CV (Unloading end) Kcal/kg | ARB CV (Kcal/kg) | 5) Gap in achievable AVF with availabe heat and actual AVF mentioned at S.N (I) in table D due to various reasons is to be furnished. Loss due to coal quality is already calaculated.Hence,need not be furnised
| 1 | Raw Coal | [5 empty] | 83444.5 |  | 4088.7736 | 3962.2803 | 3671.9491 | 83444.5 | 0 | 4088.7736 | 3962.2803 | 3671.9491 | 6) Loss due to LD backing down /RSD/Zero schedule will not appear in format as it is already covered in MERC AVF achieved
| 2 | Wash Coal
| 3 | Imported Coal | [5 empty] | 11804.35 |  | 4758.3979 | 4758.3979 | 4758.3979 | 11804.35 | 0 | 4758.3979 | 4758.3979 | 4758.3979
|  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 95248.85 | 0 | 4171.7612 | 4060.9445 | 3806.5945 | 95248.85 | 0 | 4171.7612 | 4060.9445 | 3806.5945 | 8) Losses booked in the format may not match with MORM reports
| 7 | Total | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 95248.85 | 0 | 4171.7612 | 4060.9445 | 3806.5945 | 95248.85 | #DIV/0! | 4171.7612 | 4060.9445 | 3806.5945
B | Coal Consumption details
| S.N | Source | `
|  |  | Qty (MT) | Landed cost (Rs/MT) | As billed Eq CV (loading end) Kcal/kg | Eq CV (Unloading end) Kcal/kg | ARB CV after moisture correction (Kcal/kg) | Bunkered CV tested at TPS (Kcal/kg) | ARB CV allowable as per norm (Kcal/kg) | Bunker CV allowable as per norm (Kcal/kg) | Add Gr slippage + M loss than allowable | Add stack loss than allowable
| 1 | Raw Coal | 60489 | 0 | 4088.7736 | 3962.2803 | 3671.9491 | 3115.9574 | 3671.9491 |  |  |  | 416.8245
| 2 | Wash Coal
| 3 | Imported Coal | 3861 | 0 | 4758.3979 | 4758.3979 | 4758.3979 | 3900 | 4758.3979
|  |  | 64350 | 0 | 4128.951 | 4010.0474 | 3737.136 | 3163 | 3737.136
| 7 | Total | 64350 | 0 | 4128.951 | 4010.0474 | 3737.136 | 3163 | 3737.136 | 3617.136 | 0 | 454.136
[6 empty] | FAC-II stack loss |  | 574.136
Note: Total 33 samples (Raw Coal 30 + Imp Coal 03 samples)
At unloading end for Raw coal 30 M/s Ravi Energie Pvt Ltd. results are available.
At loading end for raw coal 30 sample result of M/s. IGI are available.
For 03 No of Imported Coal at Loading and Unloading end, ARB from CCOTL analysis results are considered

## GCV DETAILS 660
660 MW GCV Details Feb-2025
Source/ Siding | Description | Qty | RR NO | RR DATE / BILL DATE | Loading End GCV (EM) | Unloading End GCV (ARB)
Raw Coal Opening Stock
TRANSITION
CGM | New Majri UG-OC Convrsion Mine | 4079.65 | 161005722 | 2025-01-31 | 4130 | 2458
UMSG | Makardhokra I OC Mine | 2008.63 | 151000734 | 2025-02-02 | 4041 | 4061
UMSG | Makardhokdha III OC Mine | 2074.87 | 151000734 | 2025-02-02 | 4068 | 4139
MBCB | Dhuptalla (Sasti UG to OC) | 3377.47 | 161002532 | 2025-02-03 | 4053 | 3905
MBCB | Ballarpur 3& 4 Pits UG Mine | 688.93 | 161002532 | 2025-02-03 | 5225 | 3811
UMSG | Umrer Ext OC Mine-Amb divrsion | 2002.9 | 161010186 | 2025-02-04 | 4725 | 4271
UMSG | Makardhokra I OC Mine | 1943.3 | 161010186 | 2025-02-04 | 3921 | 3892
CGM | New Majri UG-OC Convrsion Mine | 3896.9 | 161005731 | 2025-02-04 | 3570 | 3676
UMSG | Umrer Ext OC Mine-Amb divrsion | 2101.11 | 151000738 | 2025-02-05 | 4991 | 4282
UMSG | Gokul OC Mine | 1949.59 | 151000738 | 2025-02-05 | 4012 | 4398
GGS | Penganga OC Mine | 3921.5 | 161002858 | 2025-02-11 | 4359 | 3805
GGS | Penganga OC Mine | 4070.5 | 161002860 | 2025-02-13 | 4337 | 2659
UMSG | Makardhokra I OC Mine | 2069.69 | 161010198 | 2025-02-14 | 4088 | 3532
UMSG | Gokul OC Mine | 1988.01 | 161010198 | 2025-02-14 | 4029 | 3223
GGS | Penganga OC Mine | 3975.75 | 151000167 | 2025-02-15 | 4341 | 3258
UMSG | Gokul OC Mine | 1900.08 | 151000746 | 2025-02-15 | 4071 | 3469
UMSG | Makardhokra I OC Mine | 2005.22 | 151000746 | 2025-02-15 | 4026 | 3411
UMSG | Makardhokra I OC Mine | 3876.3 | 161010200 | 2025-02-16 | 4046 | 4177
GGS | Penganga OC Mine | 4005.95 | 161002862 | 2025-02-18 | 3614 | 3932
UMSG | Gokul OC Mine | 1866.56 | 161010202 | 2025-02-19 | 4045 | 3953
UMSG | Makardhokra I OC Mine | 1969.74 | 161010202 | 2025-02-19 | 4067 | 4520
GGS | Penganga OC Mine | 4101.1 | 161002866 | 2025-02-23 | 3622 | 3957
UMSG | Gokul OC Mine | 1931.22 | 151000755 | 2025-02-24 | 4041 | 4025
UMSG | Makardhokra I OC Mine | 2035.93 | 151000755 | 2025-02-24 | 4023 | 4171
GGS | Penganga OC Mine | 3724.15 | 141000109 | 2025-02-24 | 4323 | 3737
UMSG | Gokul OC Mine | 1209.18 | 151000757 | 26/02/2025 | 4022 | 3393
UMSG | Makardhokra I OC Mine | 2679.32 | 151000757 | 26/02/2025 | 4034 | 3443
GOSG | GDK 1 CSP | 3818.15 | 462001941 | 2025-02-08 | 4519 | 3857
CSPS | KCHP LINE II | 4138.25 | 262002760 | 2025-02-13 | 3165 | 2625
MSCA | GOLETI CHP,BPA | 4034.55 | 462000528 | 2025-02-18 | 4513 | 4066
|  | 83444.5 |  |  | 4088.7736 | 3671.9491
PPDP | HGIC PPDP | 3981.25 | 481000516 | 2025-02-02 | 4764.1456 | 4764.1456
PPDP | HGIC PPDP | 3845.75 | 481000519 | 2025-02-03 | 4748.7311 | 4748.7311
PPDP | HGIC PPDP | 3977.35 | 481000523 | 2025-02-04 | 4761.9914 | 4761.9914
|  | 11804.35 |  |  | 4758.3979 | 4758.3979
Note: Total 33 samples (Raw Coal 30 + Imp Coal 03 samples)
At unloading end for Raw coal 30 M/s Ravi Energie Pvt Ltd. results are available.
At loading end for raw coal 30 sample result of M/s. IGI are available.
For 03 No of Imported Coal at Loading and Unloading end, ARB from CCOTL analysis results are considered