## Sheet2
Comparsion of 660 MW units of MSPGCL
Sr. No. | Technical Parameters | Koradi 3x660MW | Bhusawal 1x660MW
1 | Technology | Super-critical | Super-critical
2 | Boiler | Mitsubhishi sliding pressure OTSC Radiant Reheat Bioler,Double Vortex type Firing | Top supported, sliding pressure supper critical, welded water wall, Spiral wound construction, Tilting tangential firing BHEL make Boiler.
3 | MS/RH Temeperatute | 565/593 ° C | 568 /596° C
4 | MS Pressure | 247 Kg/Sq.cm | 255 Kg/Sq.cm
5 | Boiler efficiancy | 87 % (100%TMCR) | 89.0% According to pTC 4 HHV basis.
6 | MD BFP | 1x30% Barrel Casing MultiStage | 2x30%
7 | TDBFP | 2x50% | 2x50%
8 | COAL MILL | Bowl Mill Vertical spindle MVM32R 6 Coal Mills Capacity- 112T/Hr. | Bowl mill vertical spindle, HP 1103 Bowl mill 8 Coal Mills Capacity-87.2 T/Hr DC Dynamic classifier
9 | LDO & HFO | Yes | Yes
10 | Condenser tube | SS304 welded | Welded SS (ASTM A 249, TP 316)
11 | ESP | No. of passes- 6 Field per pass- 9 Hoppers- 108 | No. of passes- 6 Field per pass- 9 Hoppers- 108
12 | Bottom ash evacution system | Ton Dry Basis (Tripple-V type) 296 Ton Dry Basis Clinker grinder capacity- 75 TPH (Dry basis) each | 1 refractory lined, water impounded, triple V(VVV ), section type steel fabricated having hold up volume to store bottom ash generated for 8 hrs. it has 6 outlets out of which 3 will be operating simultaneously Clincker grinder capacity- 90T/Hr.